## Apartments
HOT WATER SYSTEM:
|  |  |  | hotel |  | apartments
Heat Pump Calculation | [5 empty] | no of flats
Sl. No. | Extracts | Data | Units
1 | Number of Flats | 266 | No's
2 | Occupancy in each Flats | 2 | No's
3 | Total Number of occupants | 532 | No's
4 | Total quantity of water is consumed per person | 40 | Liters | 20 30
5 | Tot hot water requirement | 21280 | Liters
6 | Diversity 70% (m) | 14896 | Liters | 70 75 80%
7 | Average No. of Hours of Working (hr) | 7.5 | Hrs | 5 6 7
8 | Temp Rise (11-60deg C) | 49 | deg C | t1 initial water temp | final water temp t2 |  | t2-t1
9 | Energy required for Hot water Q=(m×c×ΔT)/hr m = mass of water (kg)Kg c = specific heat of water = 1 kcal/kg°C ΔT = temperature rise | 97320.5333 | Kcal/hr
| Equivalent Energy in KW | 113.1634 | KW
10 | Proposed Heat Pump Capacity (Each) (Heat Output) | 58 | KW
11 | Proposed Heat Pump Capacity (Each) (Heat Input) | 13.5 | KW
12 | No. of Heat Pump (Air to Water) 1250 Liters/hrs 2W+1S | 3 | Nos
| Hot water storage tank with Calorifier 3 Nos. | 3
13 | Capacity of Hot Water Storage Tanks | 5000Liters (3Nos.) (Hot water storage tank)

## hotel
HOT WATER SYSTEM:
|  |  |  | hotel |  | apartments
Heat Pump Calculation | [5 empty] | no of flats
Sl. No. | Extracts | Data | Units
1 | Number of Rooms | 266 | No's
2 | Occupancy in each Room | 2 | No's
3 | Total Number of occupants | 532 | No's
4 | Total quantity of water is consumed per person | 40 | Liters
5 | Tot hot water requirement | 21280 | Liters
6 | Diversity 70% (m) | 14896 | Liters | 70 75 80%
7 | Average No. of Hours of Working (hr) | 7.5 | Hrs | 5 6 7
8 | Temp Rise (11-60deg C) | 49 | deg C | t1 initial water temp | final water temp t2 |  | t2-t1
9 | Energy required for Hot water Q=(m×c×ΔT)/hr m = mass of water (kg)Kg c = specific heat of water = 1 kcal/kg°C ΔT = temperature rise | 97320.5333 | Kcal/hr
| Equivalent Energy in KW | 113.1634 | KW
10 | Proposed Heat Pump Capacity (Each) (Heat Output) | 58 | KW
11 | Proposed Heat Pump Capacity (Each) (Heat Input) | 13.5 | KW
12 | No. of Heat Pump (Air to Water) 1250 Liters/hrs 2W+1S | 3 | Nos
| Hot water storage tank with Calorifier 3 Nos. | 3
13 | Capacity of Hot Water Storage Tanks | 5000Liters (3Nos.) (Hot water storage tank)

## Hospitals
HOT WATER SYSTEM:
|  |  |  | hotel |  | apartments
Heat Pump Calculation | [5 empty] | no of flats
Sl. No. | Extracts | Data | Units
1 | Number of Flats | 1 | No's
2 | Occupancy in each Flats | 5 | No's
3 | Total Number of occupants | 5 | No's
4 | Total quantity of water is consumed per person | 40 | Liters | 20 30
5 | Tot hot water requirement | 200 | Liters
6 | Diversity 70% (m) | 140 | Liters | 70 75 80%
7 | Average No. of Hours of Working (hr) | 7.5 | Hrs | 5 6 7
8 | Temp Rise (11-60deg C) | 49 | deg C | t1 initial water temp | final water temp t2 |  | t2-t1
9 | Energy required for Hot water Q=(m×c×ΔT)/hr m = mass of water (kg)Kg c = specific heat of water = 1 kcal/kg°C ΔT = temperature rise | 914.6667 | Kcal/hr
| Equivalent Energy in KW | 1.0636 | KW
10 | Proposed Heat Pump Capacity (Each) (Heat Output) | 58 | KW
11 | Proposed Heat Pump Capacity (Each) (Heat Input) | 13.5 | KW
12 | No. of Heat Pump (Air to Water) 1250 Liters/hrs 2W+1S | 3 | Nos
| Hot water storage tank with Calorifier 3 Nos. | 3
13 | Capacity of Hot Water Storage Tanks | 5000Liters (3Nos.) (Hot water storage tank)